## Start Here
Battery Sizing Calculator
Free companion tool to Chapter 5: Choosing a Battery
How to use it
1. Datasheets: enter your battery module's and inverter's figures. The example is a 4.8 kWh, 48 V LFP module on a 12 kW inverter.
2. Energy: work out how much energy you need for each job: outage backup, covering your evenings, or off-grid.
3. Power: check the batteries can deliver your biggest load, and see what each number of modules can supply.
4. My Bank: choose how many modules you'll install. It checks energy, power, charging and expansion, and gives the inverter settings
and the current your cables and fused isolator must handle.
Colour key
Yellow cells, blue text: you type here. The example values are there to overwrite.
Grey cells: calculated, don't overwrite.
Green = OK. Amber = works, but harder on the batteries or worth checking. Red = not enough, or over a limit.
Important
This is a planning tool. Cable sizes, fuse and isolator ratings, and inverter settings must be confirmed by a qualified installer
using the manufacturers' instructions and your local wiring rules. Earth every battery casing and rack (Chapter 5, section 5.8).

## My Bank
My Bank
Choose how many modules you'll install, and check everything at once
Number of modules I'll install | 2
Your bank
Nominal capacity | 9.6
Usable capacity | 9.12
Power at recommended rate | 4.8
Power at maximum rate | 9.6
Checks
Outage backup | OK: covers your essentials, with 6.1 kWh to spare
Covering your evenings | OK: covers your whole evening
Off-grid | NOT ENOUGH for off-grid (need 11 modules)
Biggest load in an outage | WORKING HARD: above recommended rate, shortens battery life
Expansion | OK: room for 14 more modules
Inverter battery current | OK
Settings and protection
Set inverter maximum CHARGE current to | 100 | Uses the battery maker's recommended rate. Update these settings every time you add modules.
Set inverter maximum DISCHARGE current to | 100
Cables and fused isolator must carry at least | 200 | At the batteries' maximum current, capped by the inverter. Your installer sizes the actual cable and fuse.
…and for your planned final bank of | 3
Final bank: cables and fused isolator must carry at least | 250 | Size cables, busbars and the fused isolator for the final bank, or plan to upgrade them when you expand.
Every battery casing and rack must be earthed. Ask your installer to show you the earth connection on each one (Chapter 5, section 5.8).

## Datasheets
Datasheets
Copy these from your battery and inverter datasheets
Battery module | Value | Unit
Model | Pylontech US5000
Nominal capacity | 4.8 | kWh
Usable capacity | 4.56 | kWh | If only depth of discharge is given: nominal kWh × DoD (e.g. 4.8 × 0.95 = 4.56).
Nominal voltage | 48 | V
Recommended charge/discharge current | 50 | A | Often given as a C-rate: 0.5C on a 100 Ah module = 50 A.
Maximum continuous current | 100 | A
Maximum modules in parallel | 16 |  | Check the exact model; this varies widely between brands (Chapter 5, section 5.4).
Inverter | Value | Unit
Model | Sunsynk 12 kW
Continuous output | 12 | kW
Maximum battery charge/discharge current | 250 | A | High-voltage inverters often give this in kW instead: divide kW × 1000 by the battery voltage.
Inverter efficiency (allowance) | 95%

## Energy
Energy
How much energy does each battery job need?
Job 1: Backup for outages (essential loads)
Essential load | Average power (W) | Qty | Hours needed in an outage | kWh
Fridge-freezer (average) | 50 | 1 | 12 | 0.6 | Fridges cycle on and off: use the average, not the label rating.
Wi-Fi router + fibre box | 12 | 1 | 12 | 0.144 | Hours: how long your typical outage lasts, or one night.
Alarm system | 15 | 1 | 12 | 0.18
LED lights (living areas) | 9 | 10 | 5 | 0.45
Security lights | 10 | 4 | 10 | 0.4
TV + decoder | 120 | 1 | 3 | 0.36
Laptop | 90 | 1 | 3 | 0.27
Phone chargers | 10 | 4 | 2 | 0.08
Gate motor | 300 | 1 | 0.2 | 0.06
Total essential energy for one outage |  |  |  | 2.544
Job 2: Covering your evenings
Night-time kWh per day (from your Load Audit or Savings Estimator) |  |  |  | 6.6
Job 3: Off-grid
Total daily use (kWh) |  |  |  | 21.8
Days of backup for cloudy weather |  |  |  | 2 | Typically 2 to 3 days.
Summary
Battery job | Energy needed (kWh) |  | Usable capacity needed (kWh) | Modules needed
Backup for outages | 2.544 |  | 2.6779 | 1
Covering your evenings | 6.6 |  | 6.9474 | 2
Off-grid | 43.6 |  | 45.8947 | 11
Usable capacity needed = energy needed ÷ inverter efficiency. Modules = usable capacity needed ÷ usable capacity per module, rounded up.

## Power
Power
Can the batteries deliver your biggest load? (the C-rate check)
Biggest realistic load during an outage | 6 | e.g. kettle + microwave + lights. Use the Inverter Sizing Calculator's Loads sheet.
Battery current needed | 125
Modules needed at the recommended rate | 3
Modules needed at the maximum rate | 2
Battery current for the inverter at full output | 250
Modules to run the inverter at full output (recommended rate) | 5 | Below this, the inverter can't deliver its full rating from the battery alone.
Modules | Power at recommended rate (kW) | Power at maximum rate (kW) | Share of inverter (recommended) | Charge acceptance (kW)
1 | 2.4 | 4.8 | 20% | 2.4
2 | 4.8 | 9.6 | 40% | 4.8
3 | 7.2 | 12 | 60% | 7.2
4 | 9.6 | 12 | 80% | 9.6
5 | 12 | 12 | 100% | 12
6 | 12 | 12 | 100% | 12
7 | 12 | 12 | 100% | 12
8 | 12 | 12 | 100% | 12
9 | 12 | 12 | 100% | 12
10 | 12 | 12 | 100% | 12
11 | 12 | 12 | 100% | 12
12 | 12 | 12 | 100% | 12
13 | 12 | 12 | 100% | 12
14 | 12 | 12 | 100% | 12
15 | 12 | 12 | 100% | 12
16 | 12 | 12 | 100% | 12
Charge acceptance: how much surplus solar the bank can absorb at its recommended rate. Above this, surplus is exported or wasted.
Power is capped by the inverter's maximum battery current.