## Start Here
Inverter Sizing Calculator
Free companion tool to Chapter 4: Choosing an Inverter
How to use it
1. Datasheets: type in your panel's and inverter's figures (both datasheets list them). The example is a 600 W panel on a Sunsynk 12 kW.
2. Strings: say how many panels go in each string, and how many strings on each MPPT. Every check turns green, amber or red.
3. Loads & Surge: list what might run at the same time during an outage. It checks the inverter's continuous and surge ratings.
4. Features: tick what you need and what the inverter offers, to spot gaps before you buy.
Colour key
Yellow cells, blue text: you type here. The example values are there to overwrite.
Grey cells: calculated, don't overwrite.
Green = OK. Amber = works, but you lose some output or should check. Red = not allowed or not enough.
Important
This is a planning tool, not a design. The cold and hot voltage allowances are simple rules of thumb (Chapter 4).
Your installer must confirm the final string design for your climate, using the exact datasheets, before anything is connected.

## Datasheets
Datasheets
Copy these from your panel and inverter datasheets
Solar panel | Value | Unit
Model | JA Solar JAM66D45-600/LB
Maximum power (Pmax) | 600 | W
Open-circuit voltage (Voc) | 47.7 | V
Voltage at max power (Vmp) | 39.44 | V
Short-circuit current (Isc) | 15.95 | A
Current at max power (Imp) | 15.21 | A
Inverter | Value | Unit
Model | Sunsynk 12 kW (SUNSYNK-12K-SG02LP1)
Continuous output | 12 | kW | Surge is often given as '2× rated for 10 s' — enter it in kW (e.g. 2 × 12 = 24).
Surge output (short peak) | 24 | kW
Maximum DC input voltage | 500 | V
MPPT working range: lowest | 150 | V
MPPT working range: highest | 425 | V
Number of MPPTs | 3
Max strings per MPPT | 2
Max operating current per MPPT | 26 | A | Number of strings each MPPT can take, e.g. '2+2+2' means 3 MPPTs × 2 strings.
Max short-circuit current per MPPT | 44 | A
Max solar array | 18 | kW
Weather allowances (rules of thumb) | Value
Cold-morning voltage rise | 10% |  | Allow ~10% above Voc for cold mornings. Use more in very cold climates.
Hot-day voltage drop | 12% |  | Working voltage falls ~12% on a hot afternoon. Use more in very hot climates.

## Strings
String Check
How many panels per string, and how many strings per MPPT
Allowed string length for this panel and inverter:
Shortest string (stays in working range on a hot day) |  |  |  | 5
Longest string (stays under max DC voltage on a cold morning) |  |  |  | 9
MPPT | Panels per string | Strings on this MPPT | Cold-morning open-circuit voltage (V) | Normal working voltage (V) | Hot-day working voltage (V) | Max voltage check | Working range check | Operating current (A) | Current check | Short-circuit current (A) | Safety current check | Array power (kW) | Panels
1 | 7 | 1 | 367.29 | 276.08 | 242.9504 | OK | OK | 15.21 | OK | 15.95 | OK | 4.2 | 7
2 | 6 | 1 | 314.82 | 236.64 | 208.2432 | OK | OK | 15.21 | OK | 15.95 | OK | 3.6 | 6
3
4
5
6
Totals
Total panels | 13 |  | Leave unused MPPT rows blank. Each MPPT should carry identical strings on one roof face (Chapter 4, section 4.5).
Total array (kW) | 7.8
Array check | OK
Solar-to-inverter ratio | 0.65
Ratio note | OK: room to add panels later

## Loads & Surge
Loads & Surge
Will the inverter cope with what you run at the same time during an outage?
What might run at the same time | Running power (W) | Motor or compressor? (Y/N) | Start-up multiplier | Extra power at start-up (W)
Water heater element | 3000 | N |  | 0
Kettle | 2000 | N |  | 0
Microwave | 1000 | N |  | 0
Fridge-freezer | 150 | Y | 3 | 300
Pool pump | 750 | Y | 3 | 1500
Lights | 150 | N |  | 0
TV, Wi-Fi, chargers | 200 | N |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
Continuous load (everything above running together) | 7.25
Biggest single start-up surge on top | 1.5
Peak demand at the worst moment | 8.75
Inverter continuous output | 12
Inverter surge output | 24
Continuous check | OK
Surge check | OK
Suggested minimum inverter size | 10
The suggested size adds 25% headroom and never goes below 8 kVA, the sensible minimum for most homes today (Chapter 4, section 4.4).
When the grid is on, a hybrid inverter can often pass grid power through for bigger peaks. These checks are for outages, when the inverter is on its own.
Note on D4: Motors and compressors briefly draw 2–3× (sometimes more) their running power when starting. 3× is a safe default.

## Features
Features Checklist
Tick what you need, then what the inverter you're quoted actually offers
Feature | Why you might want it | Do I need it? | Does it have it? | Result
Battery-ready (hybrid) | Backup during outages; store solar for the evening
Correct phase (single or three) | Must match your home's supply
Enough MPPTs for my roof faces | One MPPT per roof face or direction
Time-of-use scheduling | Charge cheaply, avoid peak rates, prepare for planned outages
Generator input | Long outages or off-grid
Smart load output | Run the water heater or pool pump on surplus solar automatically
Export limiting (zero export) | Required where export isn't allowed
Fast backup switchover | Computers and Wi-Fi don't notice outages
Parallel operation | Add a second inverter later, or build three-phase
Compatible with my preferred battery | Low-voltage (48 V) or high-voltage, on the approved list
Approved for my local grid | Legal connection; insurance
Monitoring app | See production, use and faults on your phone
Local support and warranty | Someone to fix it if it fails
Must-haves missing | 0